## Sheet1
6. Connection type
□ B : PF □ C : PT □ D : NPT
□ F : BSPT □ G : BSP □ Z : Other _____
7. Unit
□ H : bar □ I : MPa □ J : kPa
8. Range
XXX : Refer to pressure unit and range table
9. Pressure connection material and dial color
□ 3 : 316SS and 2 colors
□ 7 : 316SS and 3 colors
10. Option
□ 0 : None
□ 1 : Accessories
- Standard specifications-
11. Accuracy
±1.0 % of full scale
12. Working pressure
Steady : 100% of full scale
Over range protection : 130% of full scale
13. Working temperature
Ambient : -40 ~ 65°C
Fluid : Max. 200°C
14. Degree of protection
EN60529/IEC529/IP67
15. Element type : Bourdon tube
16. Conduit connection : M20 X 1.5P
| - Main order - | [6 empty] | 17. Mat'l
| 1. Base model : P520 (Electrical contact type pressure gauge) | [6 empty] | 1) Case & Cover : Stainless steel (304SS)
| 2. Nominal diameter (mm) | [6 empty] | 2) Element : Stainless steel (316SS)
| □ 4 : 100 | [6 empty] | 3) Process connection : Stainless steel (316SS)
| 3. Type of mounting | [6 empty] | 4) Movement : Stainless steel
| □ N : Low back connection, flush, cover mounting plate | [6 empty] | 5) Windows : Safety glass
4. Contact function
□ 1 : High alarm, normal open contact
□ 2 : Low and High alarm
□ 3 : Low alarm, normal close contact
□ 4 : Two High alarm
□ 5 : Two Low alarm
□ 6 : Failsafe high and low alarm
| 5. Process connection |  |  |  |  | This drawing and the specifications are the intellectual property of WISE CONTROL INC. therefore, without a prior written consent from WISE CONTROL INC., it is strictly prohibited to reproduce the drawing or manufacture the identical products according to its specifications provided here. | THIRD ANGLE PROJECTION
□ D : 3/8"
□ E : 1/2"
WISE CONTROL INC.
5
4 | [7 empty] | SIGNATURE | DATE | DRAWING TITLE :
3 | [9 empty] | ELECTRIC CONTACTS TYPE PRESSURE GAUGE
2 | [5 empty] | UNLESS OtherWISE SPECIFIED DECIMAL DIMENSIONS ±5 ANGLE DIMENSIONS ±1˚ DIMENSIONS ARE IN MILLI METER | DESIGNED BY | K.S.LEE | 18.06.01 | DWG NO.
1 | [6 empty] | CHECKED BY | J.S.PARK | 18.06.01 | P520100N-S.T.D
NO | REASON | DATE | REVIEWED BY | CHECKED BY | APPROVED BY |  | APPROVED BY | D.M.CHO | 18.06.01
REVISION | [6 empty] | Rev.No | 0 |  | SCALE:N/S | W.T | SHEET OF