## P947-S.T.D
8. Process connection and element material
□ 3 : 316SS and 316L SS
□ Z : Monel and Monel
□ H : Hastelloy-C and Hastelloy-C
9. Option
□ 0 : None
□ 1 : Mounting bracket
□ 4 : 1/2" NPT (F) conduit connection
- Standard specifications-
10. Repeatability : ±1.0% of adjustable range
11. Working temperature
Ambient : -20 ~ 65°C
Fluid : Max. 100°C
12. Degree of protection
EN60529/IEC529/IP65
| - Main order - | [6 empty] | 13. Mat'l
| 1. Base model : P947 | [6 empty] | 1) Case & Cover : ALDC 12.1 (Silver gray painted)
| (Adjustable dead band weatherproof type pressure switch) | [6 empty] | 14. Contact rating
| 2. Deadband | [6 empty] | - SPDT contact rating -
| □ A : Adjustable (Within 8 ~ 20% of adjustable range) | [6 empty] | AC 125V / 250V, 15A
| 3. Switch form | [6 empty] | DC 125V, 0.4A for resistance load
| □ 1 : One SPDT □ 2 : Two DPDT (Only single setpoint) | [6 empty] | DC 125V, 0.03A for inductive load
| 4. Process connection | [6 empty] | - DPDT contact rating -
| □ C : 1/4" □ D : 3/8" □ E : 1/2" | [6 empty] | Resistance load |  |  | Inductive load
| 5. Connection type | [6 empty] | AC 125 V / 250 V, 10 A |  |  | AC 125 V, 6 A /AC 250 V, 4 A
| □ B : PF □ C : PT | [6 empty] | DC 125 V, 0.5 A |  |  | DC 125 V, 0.05 A
| □ D : NPT □ E : NPT (F) | [6 empty] | DC 8 V, 10 A |  |  | DC 8 V, 6 A
| 6. Unit | [6 empty] | DC 14 V, 10 A |  |  | DC 14 V, 6 A
| □ H : bar □ I : MPa □ J : kPa □ S : mbar | [6 empty] | DC 30 V, 10 A |  |  | DC 30 V, 4 A
| 7. Setting range | [6 empty] | 15. Conduit connection : 3/4" PF (F)
XXX : Refer to pressure range table
[6 empty] | This drawing and the specifications are the intellectual property of WISE CONTROL INC. therefore, without a prior written consent from WISE CONTROL INC., it is strictly prohibited to reproduce the drawing or manufacture the identical products according to its specifications provided here. |  | THIRD ANGLE PROJECTION
WISE Control Inc.
[9 empty] | SIGNATURE | DATE |  | DRAWING TITLE :
[7 empty] | PREPARED BY |  | J.S.PARK | 18.06.01 |  | Adjustable dead band weatherproof type P/S
Unless otherwise specified Decimal dimensions ±5 Angle dimensions ±1° Dimensions are in milli meter
3 | [6 empty] | REVIEWED BY |  | S.M.JUNG | 18.06.01
2 | [11 empty] | DWG NO.
1 | [6 empty] | APPROVED BY |  | D.M.CHO | 18.06.01 |  | P947-S.T.D
NO | REASON | DATE | PREPARED BY | REVIEWED BY | APPROVED BY
REVISION | [6 empty] | REV. NO. |  | 0 |  |  | SCALE: N/S | W.T. | SHEET OF
HEAD
ELEMENT