## P954
9. Options
[16 empty] | □ | 1 : Wall mounting bracket |  |  | □ | 2 : 2" mounting bracket
10. Conduit connection
[16 empty] | □ | T2 : 1/2" NPT(F) |  |  | □ | T3 : 3/4" NPT(F)
[16 empty] | □ | T6 : 1" NPT(F) |  |  | □ | T9 : M20X1.5P(F)
11. Material for cable gland
[16 empty] | □ | 00 : None
[16 empty] | □ | M7 : Ex-proof Ni plate brass |  |  | □ | MB : Ex proof 316SS
12. Ambient temperature (°C)
[16 empty] | □ | 1 : -25~65 °C (O-ring material: Viton)
[16 empty] | □ | 2 : -40~65 °C (O-ring material: Silicone)
- Standard specifications-
13. Element type : Diaphragm
14. Mat'l
1) Case & Cover : ALDC 12.1 (Silver gray finished aluminium)
2) Element : Stainless steel (316L SS), Monel, Hastelloy-C
15. Working temperature
Fluid : Max.100°C
16. Dead band
Fixed
One SPDT : Approx. 5% adjustable range
Two SPDT : Approx. 10% of adjustable range
17. Contact : Micro contact type
18. Contact rating
|  | - Main order - | [13 empty] | SPDT Contact rating
|  | 1. Base model : P954 (Explosion proof pressure switch) | [13 empty] | AC 125V / 250V, 15A
|  | 2. Switch form | [13 empty] | DC 125V, 0.5A for resistance load
|  | □ | 1 : One SPDT |  | □ | 2 : Two SPDT (Only available with single setpoint) | [9 empty] | DC 125V, 0.03A for inductive load
|  | 3. Repeatability | [13 empty] | 19. Conduit connection : 3/4" NPT(F)
|  | □ | A1 : ±1.0 % of adjustable range | [5 empty] | □ | A5 : ±0.5 % of adjustable range | [5 empty] | 20. Certificates
|  | 4. Process connection | [13 empty] | ATEX II 2G Ex db IIC T6 Gb / II 2D Ex tb IIIC T85°C Db IP67
|  | □ | C : 1/4" | □ | D : 3/8" |  | □ | E : 1/2" | [7 empty] | IECEx Ex db IIC T6 Gb / Ex tb IIIC T85°C Db IP67
|  | 5. Connection type | [13 empty] | KCS Ex db IIC T6 Gb / Ex tb IIIC T85°C Db
|  | □ | B : PF | □ | C : PT |  | □ | D : NPT |  | □ | E : NPT(F) - 1/2" NPT(F) Only
|  | 6. Unit | [12 empty] | This drawing and the specifications are the intellectual property of WISE CONTROL INC. therefore, without a prior written consent from WISE CONTROL INC., it is strictly prohibited to reproduce the drawing or manufacture the identical products according to its specifications provided here. |  | THIRD ANGLE PROJECTION
|  | □ | H : bar | □ | I : MPa |  | □ | J : kPa |  | □ | K : psi
7. Range : XXX : Refer to pressure unit and range table
|  | 8. Pressure connection / Element material | [18 empty] | WISE Control Inc.
|  | □ | 3 : 316SS / 316L SS |  |  | □ | L : 316SS / Hastelloy-C |  |  |  |  | □ | Z : Monel / Monel |  |  |  |  | SIGNATURE | DATE |  | DRAWING TITLE : Explosion proof pressure switch
[16 empty] | PREPARED BY |  | S.H.KIM | 23.09.06
[15 empty] | Unless otherwise specified Decimal dimensions ±2 Angle dimensions ±1° Dimensions are in milli meter | [5 empty] | MODEL : P954
5 | [15 empty] | REVIEWED BY |  | J.S.PARK | 23.09.06
4 | [20 empty] | PROJECT : -
3
2 | [15 empty] | APPROVED BY |  | H.J.KIM | 23.09.06 |  | DWG NO. : P954MID-S.T.D
1
NO | REASON | [5 empty] | DATE |  |  | PREPARED BY |  |  | REVIEWED BY | APPROVED BY
REVISION | [15 empty] | REV. NO. |  | 0 |  |  | SCALE: N/S | W.T. | SHEET OF
HEAD
ELEMENT