## 1
8. Pressure connection / Element material
[16 empty] | □ | 3 : 316SS / 316L SS |  |  | □ | Z : Monel / Monel
[16 empty] | □ | L : 316SS / Hastelloy-C |  |  | □ | H : Hastelloy-C / Hastelloy-C
[16 empty] | □ | K : 316SS / Monel
9. Option
[16 empty] | □ | 0 : None
[16 empty] | □ | 1 : 3 way / 5 way manifold valve
-Standard specifications-
10. Element type : Diaphragm
11. Mat'l
1) Case & Cover : ALDC 12.1 (Silver gray finished aluminium)
2) Element : Stainless steel (316L SS)
Monel, Hastelloy-C
VITON(Up to 4 KPa adjustable range)
12. Working temperature
Ambient : -40 ~ 65°C
Fluid : Max.100°C
13. Static pressure : Max. 5 MPa
14. Repeatability : ±1.0% of Adjustable range
15. Dead band
Fixed
One SPDT : Approx. 5% adjustable range
Two SPDT : Approx. 10% of adjustable range
16. Contact
Micro contact type
17. Contact rating
SPDT Contact rating
|  | - Main order - | [13 empty] | AC 125V / 250V, 15A
|  | 1. Base model | [13 empty] | DC 125V, 0.4A for resistance load
|  | ■ | P970 (Explosion proof type differential pressure switch) | [12 empty] | DC 125V, 0.03A for inductive load
|  | 2. Switch form | [13 empty] | 18. Conduit connection
|  | □ | 1 : One SPDT | [12 empty] | 3/4" NPT(F)
|  | □ | 2 : Two SPDT (Only available with single setpoint) | [12 empty] | 19. Certificates
|  | 3. Unused character : B3 (None) | [13 empty] | KCS Ex d IIC T6
|  | 4. Process connection : ■ : C 1/4" | [13 empty] | ATEX II 2G Ex d IIC T6 Gb
|  | 5. Connection type : ■ : D : NPT(F) | [13 empty] | IECEx Ex d IIC T6 Gb
6. Unit
|  | □ | H : bar | □ | I : MPa | □ | J : kPa |  | □ | S : mbar |  |  |  | This drawing and the specifications are the intellectual property of WISE CONTROL INC. therefore, without a prior written consent from WISE CONTROL INC., it is strictly prohibited to reproduce the drawing or manufacture the identical products according to its specifications provided here. | THIRD ANGLE PROJECTION
7. Range : XXX : Refer to pressure unit and range table
5 | [21 empty] | WISE CONTROL INC.
4 | [21 empty] | DRAWING TITLE : EXPLOSION PROOF
3 | [17 empty] | SIGNATURE | DATE |  |  |  |  | D/P SWITCH
2 | [13 empty] | UNLESS OtherWISE SPECIFIED DECIMAL DIMENSIONS ±5 ANGLE DIMENSIONS ±1˚ DIMENSIONS ARE IN MILLI METER | DESIGNED BY |  |  | K.S.KIM | 23.07.18 |  |  | MODEL | : P970
1 | [14 empty] | CHECKED BY |  |  | J.S.PARK | 23.07.18 |  |  | PROJECT | :
NO | REASON | [6 empty] | DATE |  |  | REVIEWED BY | CHECKED BY | APPROVED BY |  | APPROVED BY |  |  | H.J.KIM | 23.07.18 |  |  | DWG NO. | : P970MID_S.T.D
REVISION | [14 empty] | Rev. No |  |  | 0 |  |  |  | SCALE : N/S |  | W.T. | SHEET OF