## A6230-01(F.P welding)
Flange Facings("X")
F
□ 32
□ 35
[15 empty] | d1 | d2 | d3
[15 empty] | □ 7 | □ 14 | □ 23
[12 empty] | D1 |  |  | □ 9 | □ 16
[12 empty] | □ PT 1/2" |  |  | □ 10 | □ 17
|  | 1. Model : A6230 (Tapered bar stock (F.P welding)) | [9 empty] | □ NPT 1/2" |  |  | □ 12 | □ 19
Type : Bar stock thermowell with flange connection
|  | 2. Material of well : | □ 304SS | □ 316SS | □ Other
|  | Flange : | □ 304SS | □ 316SS | □ Other |  |  |  | Tag no. |  |  | Length(mm) |  | Flange rating |  |  | Q'TY
[12 empty] | T | U
*Note
1. I.D.(ød1)/O.D.(ød2) eccentricity : within ±10% of thinnest wall thickness
2. “T” length is designed with 70 mm or longer in case of flange thickness more than 28 mm
(flange thickness is more than 50mm, please contact the head office before selecting.)
3. Linear taper design is available up to under 1,000 mm of “U” length.(refer to DWG No. A6110-02).
More than 1,000 mm has two steps design, upper parallel and 300 mm tapered to the tip
|  | 4. Root dia(∅d3) basic dimension ∅23 |  |  |  |  | This drawing and the specifications are |  | THIRD ANGLE PROJECTION
|  | (Need to check the inner diameter of the thermowell insertion nozzle.) |  |  |  |  | the intellectual property of WISE
CONTROL INC. Therefore, without a prior
written consent from WISE CONTROL INC.,
[7 empty] | it is strictly prohibited to reproduce the | [5 empty] | WISE Control Inc.
drawing or manufacture the identical
[7 empty] | products according to its specifications |  |  | SIGNATURE | DATE |  | DRAWING TITLE : |  | THERMOWELL
provided here.
[8 empty] | PREPARED BY |  | S.M.JUNG | 2023-05-25 |  | MODEL : | A6230
3 | [7 empty] | REVIEWED BY |  | H.J.KIM | 2023-05-25 |  | PROJECT : -
2
1 | [7 empty] | APPROVED BY |  | H.J.KIM | 2023-05-25 |  | DWG NO. : | A6230-01
NO | REASON |  | DATE | PREPARED BY | REVIEWED BY | APPROVED BY
REVISION | [7 empty] | REV. NO. |  | 0 |  |  | SCALE: N/S |  |  | W.T. | SHEET OF
HEAD
ELEMENT