## R120A-NL-01(Nipple)
[11 empty] | GENERAL SPECIFICATION | [7 empty] | ORDERING INFORMATION
[10 empty] | 1. Head | [6 empty] | 1. Model : R12 |  | □1 (Single, 2-Wire)
[10 empty] | Material : Aluminum alloy(Standard) | [8 empty] | □2 (Double, 4-Wire)
[11 empty] | Option : | □304SS |  | □316SS |  |  | 2. Head Type : General (Weatherproof) & Tip shape
[10 empty] | Surface color : Metallic silver | [6 empty] | □ A : Ungrounded |  |  | □ C : Grounded |  |  | □ E : Exposed
[10 empty] | Construction : Weatherproof | [6 empty] | 3. Element(Tolerance)
[10 empty] | 2. Temperature transmitter | [6 empty] | * Grade : Standard 0.75 / 0.5("E","B")
[17 empty] | □ K : K | □ J : J | □ T : T | □ E : E | □ N : N | □ B : B
[10 empty] | * Transmitter option |  |  |  |  | WIRING DRAWING |  | □ R : R(0.25) |  | □ S : S(0.25)
[10 empty] | (Hart temperature transmitter) |  |  |  |  | <Temperature transmitter : T900> |  | * Grade : Special 0.4
[10 empty] | □ TA : Customer supply | [6 empty] | □ 1 : K | □ 2 : J | □ 3 : T | □ 4 : E | □ 5 : N | □ Z : Other
[10 empty] | □ TC : T/T End User Field Assembly | [6 empty] | 4. Sheath material
[10 empty] | □ TD : T900 (WISE) | [6 empty] | □ 2 : Inconel 600 |  | □ 3 : 310SS
[17 empty] | □ 4 : 446SS |  | □ 5 : 347SS |  | □ 6 : 321SS
[11 empty] | GENERAL SPECIFICATION | [5 empty] | □ 7 : 316L SS |  | □ 9 : Other
[10 empty] | 1. Power : 18 TO 30V, DC | [6 empty] | 5. Sheath outer diameter(ØD)
[10 empty] | 2. Output(2-Wire) : 4 ~ 20mA DC | [6 empty] | □ D9 : 3.2 |  | □ E9 : 4.8 |  | □ F9 : 6.4 |  | □G9 : 8.0
[10 empty] | 3. Measuring range : | [6 empty] | □ H9 : 9.5 |  | □ L9 : 12.7
[10 empty] | 4. Accuracy : ±0.2% of F.S. | [6 empty] | 6. Conduit connection |  |  | □ With adaptor |  | □ None
[10 empty] | 5. Range : °C | [6 empty] | □ 1 : PF 1/2" |  | □ 2 : PT 1/2" |  | □ 3 : NPT 1/2"
[17 empty] | □ 4 : PF 3/4" |  | □ 5 : PT 3/4" |  | □ 6 : NPT 3/4"
[10 empty] | 8. Thread size & material | [6 empty] | □ 8 : M20x1.5P |  | □ 9 : Other
[10 empty] | □EB : PT 1/2"(304SS) |  |  | □EC : NPT 1/2"(304SS) |  |  |  | * Conduit adaptor material :
[10 empty] | □FB : PT 3/4"(304SS) |  |  | □FC : NPT 3/4"(304SS) |  |  |  | □ Brass+Ni.plating |  |  | □ 304SS |  | □ 316SS
[10 empty] | □RB : PT 1/2"(316SS) |  |  | □RC : NPT 1/2"(316SS) |  |  |  | (Only 'PT' Thread)
[10 empty] | □SB : PT 3/4"(316SS) |  |  | □SC : NPT 3/4"(316SS) |  |  |  | 7. Mounting type(Nipple length) "A"
[10 empty] | □ZZ : Other | [6 empty] | □ T : 50 |  | □ U : 100 |  | □ V : 150
[10 empty] | 9. Insert length "L" : (mm) | [6 empty] | □ W : Other
* Nipple O.D(ØDn) : 21.7(St'd)
|  | *The Colors of each wires can be replaced with the ones of the user's choice. | [7 empty] | This drawing and the specifications are |  |  |  |  | THIRD ANGLE PROJECTION
|  | *Use PVC standard colors | [7 empty] | the intellectual property of WISE
|  |  | ELEMENT TYPE | □ EN(IEC) |  | □ ANSI |  | □ JIS( KS ) |  | CONTROL INC. Therefore, without a prior
|  |  |  | + | - | + | - | + | - | written consent from WISE CONTROL INC.,
|  |  | K | Green | White | Yellow | Red | Red | White | it is strictly prohibited to reproduce the | [8 empty] | WISE Control Inc.
|  |  | E | Purple | White | Purple | Red | Red | White | drawing or manufacture the identical
|  |  | J | Black | White | White | Red | Red | White | products according to its specifications | [5 empty] | SIGNATURE | DATE |  | DRAWING TITLE : |  | Sheathed thermocouple
|  |  | T | Brown | White | Blue | Red | Red | White | provided here. | [10 empty] | temperature transmitter
|  |  | B | Gray | White | Gray | Red | Red | White |  |  |  |  | PREPARED BY |  | S.M.JUNG | 2023-05-25 |  | MODEL : | R120
|  |  | S, R | Orange | White | Black | Red | Red | White
3 | [13 empty] | REVIEWED BY |  | H.J.KIM | 2023-05-25 |  | PROJECT : -
2
1 | [13 empty] | APPROVED BY |  | H.J.KIM | 2023-05-25 |  | DWG NO. : | R120A-NL-01(T/T)
NO | REASON |  | DATE | PREPARED BY |  | REVIEWED BY |  | APPROVED BY
REVISION | [13 empty] | REV. NO. |  | 0 |  |  | SCALE: N/S |  |  | W.T. | SHEET OF
HEAD
ELEMENT