## R220A-CF-01(Comp'fitting)
[8 empty] | GENERAL SPECIFICATION | [6 empty] | ORDERING INFORMATION
[7 empty] | 1. Head | [6 empty] | 1. Model : R22 | □1 (Single, □ 3-Wire □ 4-Wire)
[7 empty] | Material : Aluminum alloy(Standard) | [7 empty] | □2 (Double, □ 6-Wire)
[8 empty] | Option : |  | □304SS | □316SS |  |  | 2. Head Type A : General (Weatherproof)
[7 empty] | Surface color : Metallic silver | [6 empty] | 3. Element(Tolerance)
[7 empty] | Construction : Weatherproof | [6 empty] | * Pt 100 Ω at 0 ℃ |  | * JPt 100 Ω at 0 ℃
[7 empty] | 2. Temperature transmitter | [6 empty] | □ A : "B" Class(4-Wire) |  | □ B : "B" Class(4-Wire)
[14 empty] | □ C : "A" Class(4-Wire) |  | □ D : "A" Class(4-Wire)
[14 empty] | □ Q : "B" Class(3-Wire) |  | □ U : "B" Class(3-Wire)
[7 empty] | * Transmitter option |  |  |  |  | WIRING DRAWING |  | □ 9 : "A" Class(3-Wire) |  | □ 0 : "A" Class(3-Wire)
[7 empty] | (Hart temperature transmitter) |  |  |  |  | <Temperature transmitter> |  | □ Z : Other
[7 empty] | □ TA : Customer supply | [6 empty] | 4. Sheath material
[7 empty] | □ TC : T/T End User Field Assembly | [6 empty] | □ 7 : 316L SS | □ 9 : Other
[7 empty] | □ TD : T900 (WISE) | [6 empty] | 5. Sheath outer diameter(ØD)
[7 empty] | □ TF : T990 (WISE) | [6 empty] | □ D9 : 3.2 | □ E9 : 4.8 |  | □ F9 : 6.4 |  | □G9 : 8.0
[8 empty] | GENERAL SPECIFICATION |  |  |  |  | T900 | 6. Conduit connection |  | □ With adaptor |  | □ None
[7 empty] | 1. Power : 18 TO 30V, DC | [6 empty] | □ 1 : PF 1/2" | □ 2 : PT 1/2" |  | □ 3 : NPT 1/2"
[7 empty] | 2. Output(2-Wire) : 4 ~ 20mA DC | [6 empty] | □ 4 : PF 3/4" | □ 5 : PT 3/4" |  | □ 6 : NPT 3/4"
[7 empty] | 3. Measuring range : -200 ~ 850°C(T900) | [6 empty] | □ 8 : M20x1.5P | □ 9 : Other
[9 empty] | -50 ~ 400°C(T990) |  |  |  |  | * Conduit adaptor material :
[7 empty] | 4. Accuracy : ±0.2% of F.S. | [5 empty] | T990 | □ Brass+Ni.plating |  | □ 304SS |  | □ 316SS
[7 empty] | 5. Range : °C | [6 empty] | (Only 'PT' Thread)
** Note. Sheath ∅3.2, ∅4.8(Recommended use of reinforced tube) | [13 empty] | 7. Mounting type
□ P : Compression fitting
8. Thread size (material : 316SS)
[14 empty] | □ PB : PT 1/4" |  | □ PC : NPT 1/4"
[14 empty] | □ QB : PT 3/8" |  | □ QC : NPT 3/8"
[7 empty] | 9. Insert length "L" : (mm) | [6 empty] | □ RB : PT 1/2" |  | □ RC : NPT 1/2"
□ ZZ : Other
|  | *The Colors of each wires can be replaced with the ones of the user's choice. |  |  |  |  | This drawing and the specifications are |  |  |  |  | THIRD ANGLE PROJECTION
|  | *Use PVC standard colors |  |  |  |  | the intellectual property of WISE
|  | Connecting wire configuration |  | Connecting wire configuration |  |  | CONTROL INC. Therefore, without a prior
|  | □ (Ref : KS C 1603, JIS(Old)) |  | □ (Ref : JIS C 1604, IEC 60751) |  |  | written consent from WISE CONTROL INC.,
[7 empty] | it is strictly prohibited to reproduce the | [7 empty] | WISE Control Inc.
drawing or manufacture the identical
[7 empty] | products according to its specifications | [5 empty] | SIGNATURE | DATE | DRAWING TITLE : |  | Sheathed type(R.T.D)
[7 empty] | provided here. | [9 empty] | temperature transmitter
[11 empty] | PREPARED BY |  | S.M.JUNG | 2023-05-25 | MODEL : | R220
3 | [10 empty] | REVIEWED BY |  | H.J.KIM | 2023-05-25 | PROJECT : -
2
1 | [10 empty] | APPROVED BY |  | H.J.KIM | 2023-05-25 | DWG NO. : | R220A-CF-01(T/T)
NO | REASON |  | DATE | PREPARED BY | REVIEWED BY | APPROVED BY
REVISION | [10 empty] | REV. NO. |  | 0 |  | SCALE: N/S |  |  | W.T. | SHEET OF
HEAD
ELEMENT