## R840-003
ORDERING INFORMATION
[13 empty] | 1. Model : R84 | □ 5 (Single, 3-Wire)
□ 6 (Double, 6-Wire)
□ 7 (Single w/shield wire, 3-Wire)
□ 8 (Double w/shield wire, 6-Wire)
2. Certificates
□ A : ATEX II 2G Ex eb IIC Gb
□ B : IECEx Ex eb IIC Gb
□ C : ATEX II 1G Ex ia IIC T6...T3 Ga
□ D : IECEx Ex ia IIC T6...T3
□ E : KCs Ex eb IIC Gb
□ F : KCs Ex ia IIC T6...T3
|  |  | GENERAL SPECIFICATION | [9 empty] | □ Z : None
|  | 1. Type : Explosion Proof Type | [5 empty] | - Temperature class T5 : -40 °C < Tamb < 95 °C |  |  |  |  | 3. Element(Tolerance)
|  | -Resistance Temperature Detector | [5 empty] | (1) One Pt100 |  |  |  |  | * Pt 100 Ω at 0 °C
|  | 2. Model : R840 Series | [5 empty] | Ui = 30V, Ii = 55mA, Pi = 630mW |  |  |  |  | □ Q : "B" Class(3-Wire) |  | □ 9 : "A" Class(3-Wire)
|  | 3. Product type : Tip style B | [5 empty] | (2) Two Pt100 |  |  |  |  | □ Z : Other
|  | 4. Tip Material : Stainless steel | [5 empty] | Ui = 30V, Ii = 45mA (each Pt100), Pi = 760mW (together) |  |  |  |  | 4. Body Material
|  | 5. Lead Wire | [5 empty] | - Temperature class T4 : -40 °C < Tamb < 130 °C |  |  |  |  | □ 0 : 304SS | □ 1 : 316SS |  | □ 2 : 316L SS
|  | - Continuous Working Temp : -100 °C ~ 205 °C | [5 empty] | (1) One Pt100 |  |  |  |  | 5. Product type
|  | 6. Epoxy filled | [5 empty] | Ui = 30V, Ii = 55mA, Pi = 630mW |  |  |  |  | □ E8 : Tip style B
|  | - Continuous Working Temp : 260 °C | [5 empty] | (2) Two Pt100 |  |  |  |  | 6. Body outer diameter & Length : Ø5 & 13.7L
|  | 7. Tamb / Electrical data | [5 empty] | Ui = 30V, Ii = 50mA (each Pt100), Pi = 1W (together) |  |  |  |  | 7. Lead wire length(CL1/CL2) : (mm)
|  | - Temperature class T6 : -40 °C < Tamb < 75 °C | [5 empty] | - Temperature class T3 : -40 °C < Tamb < 180 °C |  |  |  |  | 8. Outer material of lead wire
|  | (1) One Pt100 | [5 empty] | (1) One Pt100 |  |  |  |  | □ C : FEP
|  | Ui = 30V, Ii = 25mA, Pi = 70mW | [5 empty] | Ui = 30V, Ii = 40mA, Pi = 255mW |  |  |  |  | □ Z : Other
|  | (2) Two Pt100 | [5 empty] | (2) Two Pt100
|  | Ui = 30V, Ii = 15mA (each Pt100), Pi = 50mW (together) | [5 empty] | Ui = 30V, Ii = 30mA (each Pt100), Pi = 260mW (together)
|  | *The Colors of each wires can be replaced with the ones of the user's choice. | [6 empty] | This drawing and the specifications are |  | THIRD ANGLE PROJECTION
|  | *Use PVC standard colors | [6 empty] | the intellectual property of WISE
|  | Connecting wire configuration |  |  | Connecting wire configuration |  |  |  | CONTROL INC. Therefore, without a prior
|  | □ (Ref : KS C 1603, JIS(Old)) |  |  | □ (Ref : JIS C 1604, IEC 60751) |  |  |  | written consent from WISE CONTROL INC.,
[9 empty] | it is strictly prohibited to reproduce the |  |  |  |  | WISE Control Inc.
drawing or manufacture the identical
[9 empty] | products according to its specifications |  |  | SIGNATURE | DATE | DRAWING TITLE : |  | Bearing temperature detector
provided here.
[10 empty] | PREPARED BY |  | S.M.JUNG | 2023-05-25 | MODEL : | R840
3 | [9 empty] | REVIEWED BY |  | H.J.KIM | 2023-05-25 | PROJECT : -
2
1 | [9 empty] | APPROVED BY |  | H.J.KIM | 2023-05-25 | DWG NO. : | R840-003
NO | REASON |  |  | DATE | PREPARED BY | REVIEWED BY | APPROVED BY
REVISION | [9 empty] | REV. NO. |  | 0 |  | SCALE: N/S |  |  | W.T. | SHEET OF
HEAD
ELEMENT