## R912F-NL-01_RS(Nipple)
[8 empty] | GENERAL SPECIFICATION | [6 empty] | ORDERING INFORMATION
[7 empty] | 1. Head | [6 empty] | 1. Model : R912 | (Single, 3-Wire) / (with T990)
[7 empty] | Material : Aluminum alloy(Standard) | [6 empty] | 2. Head Type :
[8 empty] | Option : | □ 316SS |  |  |  |  | F : Explosion proof
[7 empty] | Surface color : Metallic silver | [6 empty] | 3. Element(Tolerance)
[7 empty] | Construction : Explosion proof | [6 empty] | * Pt 100 Ω at 0 ℃
[7 empty] | Enclosure class : * See Note | [6 empty] | □ Q : "B" Class(3-Wire)
[7 empty] | * Note | [6 empty] | □ 9 : "A" Class(3-Wire)
[7 empty] | □ Ex d IIC T6 (KCs) | [6 empty] | □ Z : Other
[7 empty] | □ Ex tD A21 T85°C (KCs) | [6 empty] | 4. Sheath material |  | □ 7 : 316L SS |  | □ 9 : Other
5. Sheath outer diameter(ØD)
[8 empty] | WIRING DRAWING | [5 empty] | □ D9 : 3.2 | □ E9 : 4.8 |  | □ F9 : 6.4 |  | □ G9 : 8.0
[8 empty] | <Temperature transmitter : T990> | [5 empty] | 6. Conduit connection |  | □ With adaptor |  | □ None
[14 empty] | □ 1 : PF 1/2" | □ 3 : NPT 1/2" |  | □ 4 : PF 3/4"
[14 empty] | □ 6 : NPT 3/4" | □ 8 : M20x1.5P |  | □ 9 : Other
* Conduit adaptor material :
[14 empty] | □ Brass+Ni.plating |  | □ 316SS
7. Mounting type(Nipple length) "A"
[14 empty] | □ T : 50 | □ U : 100 |  | □ V : 150
[8 empty] | GENERAL SPECIFICATION | [5 empty] | □ W : Other
[7 empty] | 1. Power : 18 TO 30V, DC | [6 empty] | * Nipple O.D(ØDn) : 21.7(St'd)
[7 empty] | 2. Output(2-Wire) : 4 ~ 20mA DC | [6 empty] | 8. Thread size & material
[7 empty] | 3. Measuring range : -50 ~ 400°C | [6 empty] | □ EB : PT 1/2"(304SS) |  | □ EC : NPT 1/2"(304SS)
[7 empty] | 4. Accuracy : ±0.2% of F.S. | [6 empty] | □ FB : PT 3/4"(304SS) |  | □ FC : NPT 3/4"(304SS)
[7 empty] | 5. Range : |  |  | °C |  |  |  | □ RB : PT 1/2"(316SS) |  | □ RC : NPT 1/2"(316SS)
[14 empty] | □ SB : PT 3/4"(316SS) |  | □ SC : NPT 3/4"(316SS)
□ ZZ : Other
* Note. Connector type(Standard) / Drilled bar(only for nipple length 50mm) | [13 empty] | 9. Insert length "L" : (mm)
|  | *The Colors of each wires can be replaced with the ones of the user's choice. |  |  |  |  | This drawing and the specifications are |  |  |  |  | THIRD ANGLE PROJECTION
|  | *Use PVC standard colors |  |  |  |  | the intellectual property of WISE
|  | Connecting wire configuration |  | Connecting wire configuration |  |  | CONTROL INC. Therefore, without a prior
|  | □ (Ref : KS C 1603, JIS(Old)) |  | □ (Ref : JIS C 1604, IEC 60751) |  |  | written consent from WISE CONTROL INC.,
[7 empty] | it is strictly prohibited to reproduce the | [7 empty] | WISE Control Inc.
drawing or manufacture the identical
[7 empty] | products according to its specifications | [5 empty] | SIGNATURE | DATE | DRAWING TITLE : |  | Head mounting type
[7 empty] | provided here. | [9 empty] | temperature transmitter
[11 empty] | PREPARED BY |  | S.M.JUNG | 2023-05-25 | MODEL : | R912
3 | [10 empty] | REVIEWED BY |  | H.J.KIM | 2023-05-25 | PROJECT : -
2
1 | [10 empty] | APPROVED BY |  | H.J.KIM | 2023-05-25 | DWG NO. : | R912F-NL-01(RS)
NO | REASON |  | DATE | PREPARED BY | REVIEWED BY | APPROVED BY
REVISION | [10 empty] | REV. NO. |  | 0 |  | SCALE: N/S |  |  | W.T. | SHEET OF
HEAD
ELEMENT