## R920C-UN-01_TS(Union_Nipple)
[11 empty] | GENERAL SPECIFICATION | [7 empty] | ORDERING INFORMATION
[10 empty] | 1. Head | [6 empty] | 1. Model : R92 |  | □ 1, 3 (Single, 2-Wire)
[10 empty] | Material : Aluminum alloy(Standard) | [8 empty] | □ 2, 4 (Double, 4-Wire)
[11 empty] | Option : | □ 316SS |  |  |  |  | 2. Head material and tip shape type (Double conduit)
[10 empty] | Surface color : Metallic silver | [6 empty] | □ C : Ungrounded |  |  |  | □ G : Ungrounded (316SS)
[10 empty] | Construction : Explosion proof | [6 empty] | □ D : Grounded |  |  |  | □ H : Grounded (316SS)
[10 empty] | Enclosure class : *See Note | [6 empty] | 3. Element(Tolerance)
[10 empty] | *Note : Enclosure Class | [6 empty] | * Grade : Standard 0.75 / 0.5("E")
[10 empty] | □ KCs Ex d IIC T6 (R921,R922) | [6 empty] | □ K : K | □ J : J | □ T : T | □ E : E | □ N : N
[10 empty] | □ KCs Ex tD A21 T85°C (R923,R924) | [6 empty] | * Grade : Special 0.4
[10 empty] | 2. Terminal block material : PBT resin | [6 empty] | □ 1 : K | □ 2 : J | □ 3 : T | □ 4 : E | □ 5 : N
[10 empty] | 3. Spring load type | [6 empty] | 4. Sheath material
[17 empty] | □ 2 : Inconel 600 |  |  | □ 3 : 310SS |  | □ 4 : 446SS
[17 empty] | □ 5 : 347SS |  |  | □ 6 : 321SS |  | □ 7 : 316L SS
5. Sheath outer diameter(ØD)
[17 empty] | □ D9 : 3.2 |  | □ E9 : 4.8 |  | □ F9 : 6.4 |  | □ G9 : 8.0
[17 empty] | 6. Conduit connection |  |  | □ With adaptor |  | □ None
[17 empty] | □ 1 : PF 1/2" |  | □ 3 : NPT 1/2" |  | □ 4 : PF 3/4"
[17 empty] | □ 6 : NPT 3/4" |  | □ 8 : M20x1.5P |  | □ 9 : Other
* Conduit adaptor material :
[17 empty] | □ Brass+Ni.plating |  |  | □ 316SS
[10 empty] | 8. Thread size & material | [6 empty] | 7. Mounting type(Union & Nipple length) "A"
[10 empty] | □ EB : PT 1/2"(304SS) |  |  | □ EC : NPT 1/2"(304SS) |  |  |  | □ Q : 100 |  | □ R : 150 |  | □ *Y : 150(Oil sealing type)
[10 empty] | □ FB : PT 3/4"(304SS) |  |  | □ FC : NPT 3/4"(304SS) |  |  |  | □ S : Other |  |  |  | *Maximum operating pressure(1Bar)
[10 empty] | □ RB : PT 1/2"(316SS) |  |  | □ RC : NPT 1/2"(316SS) |  |  |  | * Union & nipple O.D(ØDn) : 21.7(St'd)
[10 empty] | □ SB : PT 3/4"(316SS) |  |  | □ SC : NPT 3/4"(316SS)
□ ZZ : Other
9. Insert length "L" : (mm)
* Note. Connector type(Standard) / Drilled bar(only for nipple length 100mm)
|  | *The Colors of each wires can be replaced with the ones of the user's choice. | [7 empty] | This drawing and the specifications are |  |  |  |  | THIRD ANGLE PROJECTION
|  | *Use PVC standard colors | [7 empty] | the intellectual property of WISE
|  |  | ELEMENT TYPE | □ EN(IEC) |  | □ ANSI |  | □ JIS( KS ) |  | CONTROL INC. Therefore, without a prior
|  |  |  | + | - | + | - | + | - | written consent from WISE CONTROL INC.,
|  |  | K | Green | White | Yellow | Red | Red | White | it is strictly prohibited to reproduce the | [8 empty] | WISE Control Inc.
|  |  | E | Purple | White | Purple | Red | Red | White | drawing or manufacture the identical
|  |  | J | Black | White | White | Red | Red | White | products according to its specifications | [5 empty] | SIGNATURE | DATE |  | DRAWING TITLE : |  | Sheathed thermocouple
|  |  | T | Brown | White | Blue | Red | Red | White | provided here.
|  |  | B | Gray | White | Gray | Red | Red | White |  |  |  |  | PREPARED BY |  | S.M.JUNG | 2023-05-25 |  | MODEL : | R920
|  |  | S, R | Orange | White | Black | Red | Red | White
3 | [13 empty] | REVIEWED BY |  | H.J.KIM | 2023-05-25 |  | PROJECT : -
2
1 | [13 empty] | APPROVED BY |  | H.J.KIM | 2023-05-25 |  | DWG NO. : | R920C-UN-01(TS)
NO | REASON |  | DATE | PREPARED BY |  | REVIEWED BY |  | APPROVED BY
REVISION | [13 empty] | REV. NO. |  | 0 |  |  | SCALE: N/S |  |  | W.T. | SHEET OF
HEAD
ELEMENT