## R94XC-NN-02_TS_TT(None)
[12 empty] | GENERAL SPECIFICATION | [7 empty] | ORDERING INFORMATION
[11 empty] | 1. Head | [6 empty] | 1. Model : R94 |  | □ A, E (Single, 2-Wire)
[11 empty] | Material : Aluminum alloy(Standard) | [8 empty] | □ B, F (Double, 4-Wire)
[12 empty] | Option : | □ 316SS |  |  |  |  | 2. Head material and tip shape type (Double conduit)
[11 empty] | Surface color : Metallic silver | [6 empty] | □ C : Ungrounded |  |  |  | □ G : Ungrounded (316SS)
[11 empty] | Construction : Explosion proof | [6 empty] | □ D : Grounded |  |  |  | □ H : Grounded (316SS)
[11 empty] | Enclosure class | [6 empty] | 3. Element(Tolerance)
[11 empty] | □ KCs Ex db eb IIC T6 Gb (R94A,R94B) | [6 empty] | * Grade : Standard 0.75 / 0.5("E")
[11 empty] | □ KCs Ex tD A21 T85°C (R94E,R94F) | [6 empty] | □ K : K | □ J : J | □ T : T | □ E : E | □ N : N
[11 empty] | 2. Ambient temperature | [6 empty] | * Grade : Special 0.4
[11 empty] | ■ -20 ~ +65 °C (NBR(St'd)) | [6 empty] | □ 1 : K | □ 2 : J | □ 3 : T | □ 4 : E | □ 5 : N
[11 empty] | □ -40 ~ +65 °C (Silicone) | [6 empty] | □ Z : Other
[11 empty] | 3. Insulation material for lead wires | [6 empty] | 4. Sheath material
[11 empty] | □ PVC |  |  | □ Teflon |  |  |  | □ 2 : Inconel 600 |  | □ 3 : 310SS |  | □ 4 : 446SS
[11 empty] | □ Non-asbestos |  |  | □ Outer shield |  |  |  | □ 5 : 347SS |  | □ 6 : 321SS |  | □ 7 : 316L SS
[11 empty] | □ Other | [6 empty] | □ 9 : Other
[11 empty] | 4. Jacket material for flexible tubing | [6 empty] | 5. Sheath outer diameter(ØD)
[11 empty] | □ Shrink tube |  | □ PVC coating |  |  | □ None |  | □ D9 : 3.2 |  | □ E9 : 4.8 |  | □ F9 : 6.4 |  | □G9 : 8.0
[11 empty] | 5. Mounting Bracket material : |  |  | □304SS(St'd) |  | □316L SS |  | □ H9 : 9.5 |  | □ L9 : 12.7
[18 empty] | 6. Conduit connection |  |  | □ With adaptor |  | □ None
[18 empty] | □ 3 : NPT 1/2" |  | □ 6 : NPT 3/4" |  | □ 8 : M20x1.5P
|  |  |  | Temperature transmitter | [13 empty] | □ 9 : Other
|  |  |  | 1. Power : 18 TO 30V, DC | [13 empty] | * Conduit adaptor material :
|  |  |  | 2. Output(2-Wire) : 4 ~ 20mA DC | [6 empty] | 10. Insert length "L" : (mm) | [6 empty] | □ Brass+Ni.plating |  |  | □ 316SS
| Bracket t=3 |  |  | 3. Measuring range : | [6 empty] | 11. Integral transmitter (See note 2.) | [6 empty] | 7. Lead wire length "A"(M)
| With U-Bolt(2") & Nut |  |  | 4. Accuracy : ±0.2% of F.S. | [6 empty] | □ 1 : T900 (WISE) |  |  | □ 2 : T990 (WISE)RTD only |  |  |  | □ A : 300 mm |  | □ B : 1 |  | □ C : 2 |  | □ D : 3
*Note1. Minimum lead wire length = 100 mm |  |  |  | 5. Range : °C | [6 empty] | □ 3 : TH300 (SIEMENS) |  |  | □ 4 : TTH300 (ABB) |  |  |  | □ E : 4 |  | □ F : 5 |  | □ G : Other
Note 2. Although temperature element is selected double(Duplex) type, | [10 empty] | □ 5 : YTA70 (YOKOGAWA) |  |  | □ 6 : 644H (ROSEMOUNT) |  |  |  | 8,9. Mounting & Connection type
| output of integral transmitter is single. | [9 empty] | □ 7 : Other | [6 empty] | □ AAA : None
|  | *The Colors of each wires can be replaced with the ones of the user's choice. | [8 empty] | This drawing and the specifications are |  |  |  |  | THIRD ANGLE PROJECTION
|  | *Use PVC standard colors | [8 empty] | the intellectual property of WISE
|  |  | ELEMENT TYPE |  | □ EN(IEC) |  | □ ANSI |  | □ JIS( KS ) |  | CONTROL INC. Therefore, without a prior
[5 empty] | + | - | + | - | + | - | written consent from WISE CONTROL INC.,
|  |  | K |  | Green | White | Yellow | Red | Red | White | it is strictly prohibited to reproduce the | [8 empty] | WISE Control Inc.
|  |  | E |  | Purple | White | Purple | Red | Red | White | drawing or manufacture the identical
|  |  | J |  | Black | White | White | Red | Red | White | products according to its specifications | [5 empty] | SIGNATURE | DATE |  | DRAWING TITLE : |  | Sheathed thermocouple
|  |  | T |  | Brown | White | Blue | Red | Red | White | provided here.
|  |  | B |  | Gray | White | Gray | Red | Red | White |  |  |  |  | PREPARED BY |  | S.M.JUNG | 2023-05-25 |  | MODEL : | R94X
|  |  | S, R |  | Orange | White | Black | Red | Red | White
3 | [14 empty] | REVIEWED BY |  | H.J.KIM | 2023-05-25 |  | PROJECT : -
2
1 | [14 empty] | APPROVED BY |  | H.J.KIM | 2023-05-25 |  | DWG NO. : | R94XC-NN-02(TS)TT
NO | REASON |  | DATE |  | PREPARED BY |  | REVIEWED BY |  | APPROVED BY
REVISION | [14 empty] | REV. NO. |  | 0 |  |  | SCALE: N/S |  |  | W.T. | SHEET OF
HEAD
ELEMENT