## R94XA-NN-03_RS_TT(None)
[9 empty] | GENERAL SPECIFICATION | [6 empty] | ORDERING INFORMATION
[8 empty] | 1. Head | [6 empty] | 1. Model : R94 | □ A, E (Single, □ 3-Wire □ 4-Wire)
[8 empty] | Material : Aluminum alloy(Standard) | [7 empty] | □ B, F (Double, □ 6-Wire □ 8-Wire)
[9 empty] | Option : | □ 316SS |  |  |  |  | 2. Head material and tip shape type
[8 empty] | Surface color : Metallic silver | [6 empty] | □ A : Ungrounded |  |  | □ E : Ungrounded (316SS)
[8 empty] | Construction : Explosion proof | [6 empty] | 3. Element(Tolerance)
[8 empty] | Enclosure class | [6 empty] | * Pt 100 Ω at 0 ℃ |  |  | * JPt 100 Ω at 0 ℃
[8 empty] | □ KCs Ex db eb IIC T6 Gb (R94A,R94B) | [6 empty] | □ A : "B" Class(4-Wire) |  |  | □ B : "B" Class(4-Wire)
[8 empty] | □ KCs Ex tD A21 T85°C (R94E,R94F) | [6 empty] | □ C : "A" Class(4-Wire) |  |  | □ D : "A" Class(4-Wire)
[8 empty] | 2. Ambient temperature | [6 empty] | □ Q : "B" Class(3-Wire) |  |  | □ U : "B" Class(3-Wire)
[8 empty] | ■ -20 ~ +65 °C (NBR(St'd)) | [6 empty] | □ 9 : "A" Class(3-Wire) |  |  | □ 0 : "A" Class(3-Wire)
[8 empty] | □ -40 ~ +65 °C (Silicone) | [6 empty] | □ Z : Other
[8 empty] | 3. Insulation material for lead wires | [6 empty] | 4. Sheath material |  | □ 7 : 316L SS |  | □ 9 : Other
[8 empty] | □ PVC |  |  | □ Teflon |  |  |  | 5. Sheath outer diameter(ØD)
[8 empty] | □ Non-asbestos |  |  | □ Outer shield |  |  |  | □ D9 : 3.2 | □ E9 : 4.8 |  | □ F9 : 6.4 |  | □G9 : 8.0
[8 empty] | □ Other | [6 empty] | 6. Conduit connection |  | □ With adaptor |  | □ None
[8 empty] | 4. Jacket material for flexible tubing | [6 empty] | □ 3 : NPT 1/2" | □ 6 : NPT 3/4" |  | □ 8 : M20x1.5P
[8 empty] | □ Shrink tube |  | □ PVC coating |  |  | □ None |  | □ 9 : Other
[8 empty] | 5. Mounting Bracket material : |  |  | □304SS(St'd) |  | □316L SS |  | * Conduit adaptor material : |  | □ Brass+Ni.plating |  |  | □ 316SS
7. Lead wire length "A"(M)
[15 empty] | □ A : 300 mm | □ B : 1 |  | □ C : 2 |  | □ D : 3
|  |  |  | Temperature transmitter | [10 empty] | □ E : 4 | □ F : 5 |  | □ G : Other
|  |  |  | 1. Power : 18 TO 30V, DC | [10 empty] | 8,9. Mounting & Connection type
|  |  |  | 2. Output(2-Wire) : 4 ~ 20mA DC | [10 empty] | □ AAA : None
| Bracket t=3 |  |  | 3. Measuring range : |  |  |  | 11. Integral transmitter (See note 2.) | [6 empty] | 10. Insert length "L" : (mm)
|  |  |  | 4. Accuracy : ±0.2% of F.S. |  |  |  | □ 1 : T900 (WISE) |  |  | □ 2 : T990 (WISE)RTD only
*Note1. Minimum lead wire length = 100 mm |  |  |  | 5. Range : °C |  |  |  | □ 3 : TH300 (SIEMENS) |  |  | □ 4 : TTH300 (ABB)
Note 2. Although temperature element is selected double(Duplex) type, | [7 empty] | □ 5 : YTA70 (YOKOGAWA) |  |  | □ 6 : 644H (ROSEMOUNT)
| output of integral transmitter is single. | [6 empty] | □ 7 : Other
|  | *The Colors of each wires can be replaced with the ones of the user's choice. | [5 empty] | This drawing and the specifications are |  |  |  |  | THIRD ANGLE PROJECTION
|  | *Use PVC standard colors | [5 empty] | the intellectual property of WISE
|  | Connecting wire configuration |  |  | Connecting wire configuration |  |  | CONTROL INC. Therefore, without a prior
|  | □ (Ref : KS C 1603, JIS(Old)) |  |  | □ (Ref : JIS C 1604, IEC 60751) |  |  | written consent from WISE CONTROL INC.,
[8 empty] | it is strictly prohibited to reproduce the | [7 empty] | WISE Control Inc.
drawing or manufacture the identical
[8 empty] | products according to its specifications | [5 empty] | SIGNATURE | DATE | DRAWING TITLE : |  | Sheathed type
[8 empty] | provided here. | [9 empty] | resistance temperature detector
[12 empty] | PREPARED BY |  | S.M.JUNG | 2023-05-25 | MODEL : | R94X
3 | [11 empty] | REVIEWED BY |  | H.J.KIM | 2023-05-25 | PROJECT : -
2
1 | [11 empty] | APPROVED BY |  | H.J.KIM | 2023-05-25 | DWG NO. : | R94XA-NN-03(RS)TT
NO | REASON |  | DATE |  | PREPARED BY | REVIEWED BY | APPROVED BY
REVISION | [11 empty] | REV. NO. |  | 0 |  | SCALE: N/S |  |  | W.T. | SHEET OF
HEAD
ELEMENT