## SMT3000A-NL-001(RTD)
[8 empty] | GENERAL SPECIFICATION | [5 empty] | ORDERING INFORMATION
[8 empty] | 1. Power supply |  |  |  |  | 1. Base model : SMT3000 (Smart temperature taransmitter)
[8 empty] | WTT-3000 : 10~32V DC |  |  |  |  | 2. Type : ■ A : Direct type
[8 empty] | iTEMP TMT82 : 11~42V DC |  |  |  |  | 3. Element(Tolerance)
[8 empty] | Rosemount 644H : 12~42.4V DC |  |  |  |  | □ Q : Pt 100 (B), 3-Wire |  |  | □ 9 : Pt 100 (A), 3-Wire
[8 empty] | 2. Output : 4 ~ 20mA with HART Protocol |  |  |  |  | □ A : Pt 100 (B), 4-Wire |  |  | □ C : Pt 100 (A), 4-Wire
[8 empty] | 3. Housing Material : ADC12 |  |  |  |  | 4. Sheath material
[8 empty] | 4. Protection grade : IP66&IP67 |  |  |  |  | □ 7 : 316L SS |  | □ 9 : Other
[8 empty] | 5. Certificates |  |  |  |  | 5. Sheath outer diameter(ØD)
[8 empty] | □ 0 : None | □ 1 : KCs Ex db IIC T6 Gb |  |  |  | □ D9 : 3.2 |  | □ E9 : 4.8 |  | □ F9 : 6.4 |  | □G9 : 8.0
[13 empty] | 6. Conduit connection |  |  | □ With adaptor |  | □ None
[13 empty] | □ 1 : PF 1/2" |  |  | □ 3 : NPT 1/2"
[13 empty] | □ 8 : M20x1.5P (St'd) |  |  | □ 9 : Other
[8 empty] | 10. Temperature transmitter |  |  |  |  | * Adaptor Material : □ 316SS □ Brass+Ni □ 304SS
[8 empty] | □ A : WTT-3000 (WISE) | [9 empty] | (Only weatherproof)
[8 empty] | □ B : iTEMP TMT82 (Endress+Hauser) |  |  |  |  | * Note.
[8 empty] | □ C : Rosemount 644 (EMERSON) |  |  |  |  | Adapters are applied for all sizes other than M20(St'd).
[8 empty] | 11. Measuring range (˚C) : |  |  |  |  | If explosion-proof certification is requested,
[8 empty] | 12. Display |  |  |  |  | an explosion-proof adapter is applied.
[8 empty] | □ A : PV (Temperature ˚C, ˚F) |  |  |  |  | 7. Mounting type(Nipple length) "A"
[8 empty] | □ B : Current (4~20 mA) |  |  |  |  | □ T : 50 |  | □ U : 100 |  | □ V : 150 |  | □ W : Other
[8 empty] | □ C : Persent (0~100%) |  |  |  |  | * Nipple O.D(ØDn) : Ø21.7
[8 empty] | 13. Burnout mode |  |  |  |  | 8. Thread size & material
[8 empty] | □ U : Upscale burnout (Standard) |  |  |  |  | □ EB : PT 1/2"(304SS) |  |  |  | □ EC : NPT 1/2"(304SS)
[8 empty] | □ D : Downscale burnout |  |  |  |  | □ FB : PT 3/4"(304SS) |  |  |  | □ FC : NPT 3/4"(304SS)
[8 empty] | * Lead wire length : 200 (mm) |  |  |  |  | □ RB : PT 1/2"(316SS) |  |  |  | □ RC : NPT 1/2"(316SS)
[13 empty] | □ SB : PT 3/4"(316SS) |  |  |  | □ SC : NPT 3/4"(316SS)
□ ZZ : Other
[7 empty] | ** Note. Connector type(Standard) / Drilled bar(only for nipple length 50mm) | [5 empty] | 9. Insert length "L" : mm
|  | *The Colors of each wires can be replaced with the ones of the user's choice. | [5 empty] | This drawing and the specifications are |  |  | THIRD ANGLE PROJECTION
|  | *Use PVC standard colors | [5 empty] | the intellectual property of WISE
|  | Connecting wire configuration |  | Connecting wire configuration |  |  |  | CONTROL INC. Therefore, without a prior
|  | □ (Ref : KS C 1603, JIS(Old)) |  | □ (Ref : JIS C 1604, IEC 60751) |  |  |  | written consent from WISE CONTROL INC.,
[8 empty] | it is strictly prohibited to reproduce the | [6 empty] | WISE Control Inc.
drawing or manufacture the identical
[8 empty] | products according to its specifications |  |  |  | SIGNATURE | DATE |  | DRAWING TITLE : |  | Smart temperature Transmitter
provided here.
[10 empty] | PREPARED BY |  | S.M.JUNG | 2023-05-25 |  | MODEL : | SMT3000(RTD)
3 | [9 empty] | REVIEWED BY |  | H.J.KIM | 2023-05-25 |  | PROJECT : -
2
1 | [9 empty] | APPROVED BY |  | H.J.KIM | 2023-05-25 |  | DWG NO. : | SMT3000A-NL-001(RTD)
NO | REASON |  | DATE | PREPARED BY | REVIEWED BY | APPROVED BY
REVISION | [9 empty] | REV. NO. |  | 0 |  |  | SCALE: N/S |  |  | W.T. | SHEET OF
HEAD
ELEMENT