## SMT3000C-CF-001(RTD)
GENERAL SPECIFICATION
[17 empty] | 1. Power supply | WTT-3000 : 10~32V DC
iTEMP TMT82 : 11~42V DC
Rosemount 644H : 12~42.4V DC
2. Output : 4 ~ 20mA with HART Protocol
3. Housing Material : ADC12
4. Protection grade : IP66&IP67
[17 empty] | 5. Certificates | □ None |  | □ 1 : KCs Ex db llC T6 Gb
*Sleeve
Out dia.(Ød)(mm) : ■ 12 □ Other
Length "T"(mm) : ■ 50 □ Other
*Flexible tube length "A" : mm
*Insulation material for lead wires
[17 empty] | □ A : PVC | □ B : Teflon |  | □ D : Outer shield
ORDERING INFORMATION
| 1. Base model : SMT3000(Smart temperature taransmitter) | [10 empty] | 7. Mounting type |  |  |  |  | 12. Display
| 2. Type : ■ C : Remote type | [10 empty] | ■ P : Compression fitting |  |  |  |  | □ A : PV (Temperature ˚C, ˚F)
| 3. Element(Tolerance) | [10 empty] | 8. Connection size(material : 316SS) |  |  |  |  | □ B : Current (4~20 mA)
| □ Q : Pt 100 (B), 3-Wire |  |  |  |  | □ A : Pt 100 (B), 4-Wire | [5 empty] | □ PB : PT 1/4" | □ PC : NPT 1/4" |  |  |  | □ C : Persent (0~100%)
| □ 9 : Pt 100 (A), 3-Wire |  |  |  |  | □ C : Pt 100 (A), 4-Wire | [5 empty] | □ QB : PT 3/8" | □ QC : NPT 3/8" |  |  |  | 13. Burnout mode
| 4. Sheath material | [10 empty] | □ RB : PT 1/2" | □ RC : NPT 1/2" |  |  |  | □ U : Upscale burnout (Standard)
| □ 7 : 316L SS |  |  | □ 9 : Other | [7 empty] | 9. Insert length "L" : mm |  |  |  |  | □ D : Downscale burnout
| 5. Sheath outer diameter(ØD) | [10 empty] | * Lead wire length : 200 (mm) |  |  |  |  | * Note.
| □ D9 : 3.2 |  | □ E9 : 4.8 |  | □ F9 : 6.4 |  | □G9 : 8.0 |  |  |  |  | 10. Temperature transmitter |  |  |  |  | Adapters are applied for all sizes other than M20(St'd).
| 6. Conduit connection |  |  |  | □ With adaptor |  |  | □ None |  |  |  | □ A : WTT-3000 (WISE) |  |  |  |  | If explosion-proof certification is requested,
| □ 1 : PF 1/2" |  |  |  | □ 3 : NPT 1/2" | [6 empty] | □ B : iTEMP TMT82 (Endress+Hauser) |  |  |  |  | an explosion-proof adapter is applied.
| □ 8 : M20x1.5P (St'd) |  |  |  | □ 9 : Other | [6 empty] | □ C : Rosemount 644 (EMERSON) |  |  |  |  | Additional clamping of cable shall be installed to ensure
| * Adaptor Material : □ 316SS □ Brass+Ni □ 304SS | [10 empty] | 11. Measuring range (˚C) : |  |  |  |  | that pulling and twisting is not transmitted to the terminal.
(Only weatherproof)
|  | *The Colors of each wires can be replaced with the ones of the user's choice. | [9 empty] | This drawing and the specifications are |  |  | THIRD ANGLE PROJECTION
|  | *Use PVC standard colors | [9 empty] | the intellectual property of WISE
|  | Connecting wire configuration | [5 empty] | Connecting wire configuration |  |  |  | CONTROL INC. Therefore, without a prior
|  | □ (Ref : KS C 1603, JIS(Old)) | [5 empty] | □ (Ref : JIS C 1604, IEC 60751) |  |  |  | written consent from WISE CONTROL INC.,
[12 empty] | it is strictly prohibited to reproduce the | [5 empty] | WISE Control Inc.
drawing or manufacture the identical
[12 empty] | products according to its specifications |  |  |  | SIGNATURE | DATE | DRAWING TITLE : |  | Smart temperature Transmitter
provided here.
[14 empty] | PREPARED BY |  | S.M.JUNG | 2023-05-25 | MODEL : | SMT3000(RTD)
3 | [13 empty] | REVIEWED BY |  | H.J.KIM | 2023-05-25 | PROJECT : -
2
1 | [13 empty] | APPROVED BY |  | H.J.KIM | 2023-05-25 | DWG NO. : | SMT3000C-CF-001(RTD)
NO | REASON |  |  |  |  | DATE |  | PREPARED BY |  | REVIEWED BY | APPROVED BY
REVISION | [13 empty] | REV. NO. |  | 0 |  | SCALE: N/S |  |  | W.T. | SHEET OF
HEAD
ELEMENT