## SMT3000B-UN-001(TC)
[9 empty] | GENERAL SPECIFICATION | [6 empty] | ORDERING INFORMATION
[9 empty] | 1. Power supply | [5 empty] | 1. Base model : SMT3000 (Smart temperature taransmitter)
[9 empty] | WTT-3000 : 10~32V DC | [5 empty] | 2. Type : ■ B : Direct&Spring loaded type
[9 empty] | iTEMP TMT82 : 11~42V DC | [5 empty] | 3. Element(Tolerance)
[9 empty] | Rosemount 644H : 12~42.4V DC | [5 empty] | □ K : K(0.75) |  | □ J : J(0.75) |  | □ T : T(0.75)
[9 empty] | 2. Output : 4 ~ 20mA with HART Protocol | [5 empty] | □ N : N(0.75) |  | □ E : E(0.5)
[9 empty] | 3. Housing Material : ADC12 | [5 empty] | □ B : B(0.5) |  | □ S : S(0.25) |  | □ R : R(0.25)
[9 empty] | 4. Protection grade : IP66&IP67 | [5 empty] | □ 1 : K(0.4) |  | □ 2 : J(0.4) |  | □ 3 : T(0.4)
[9 empty] | 5. Certificates | □ 0 : None | □ 1 : KCs Ex db IIC T6 Gb |  |  |  | □ 5 : N(0.4) |  | □ 4 : E(0.4)
4. Sheath material
[9 empty] | 8. Thread size & material | [5 empty] | □ 2 : Inconel 600 |  |  | □ 3 : 310SS |  | □ 4 : 446SS
[9 empty] | □ EB : PT 1/2"(304SS) |  | □ EC : NPT 1/2"(304SS) |  |  |  | □ 5 : 347SS |  |  | □ 6 : 321SS |  | □ 7 : 316L SS
[9 empty] | □ FB : PT 3/4"(304SS) |  | □ FC : NPT 3/4"(304SS) |  |  |  | 5. Sheath outer diameter(ØD)
[9 empty] | □ RB : PT 1/2"(316SS) |  | □ RC : NPT 1/2"(316SS) |  |  |  | □ D9 : 3.2 |  | □ E9 : 4.8 |  | □ F9 : 6.4 |  | □G9 : 8.0
[9 empty] | □ SB : PT 3/4"(316SS) |  | □ SC : NPT 3/4"(316SS) |  |  |  | 6. Conduit connection |  |  | □ With adaptor |  | □ None
[9 empty] | □ ZZ : Other | [5 empty] | □ 1 : PF 1/2" |  | □ 3 : NPT 1/2"
[9 empty] | 9. Insert length "L" : mm | [5 empty] | □ 8 : M20x1.5P (St'd) |  |  | □ 9 : Other
[9 empty] | 10. Temperature transmitter | [5 empty] | * Adaptor Material : □ 316SS □ Brass+Ni □ 304SS
[9 empty] | □ A : WTT-3000 (WISE) | [10 empty] | (Only weatherproof)
[9 empty] | □ B : iTEMP TMT82 (Endress+Hauser) | [5 empty] | * Note.
[9 empty] | □ C : Rosemount 644 (EMERSON) | [5 empty] | Adapters are applied for all sizes other than M20(St'd).
[9 empty] | 11. Measuring range (˚C) : | [5 empty] | If explosion-proof certification is requested,
[9 empty] | 12. Display | [5 empty] | an explosion-proof adapter is applied.
[9 empty] | □ A : PV (Temperature ˚C, ˚F) |  |  | □ B : Current (4~20 mA) |  |  | 7. Mounting type(Union&Nipple length) "A"
[9 empty] | □ C : Persent (0~100%) | [5 empty] | □ Q : 100 |  | □ R : 150 |  | □ S : Other
[9 empty] | 13. Burnout mode | [5 empty] | * Nipple O.D(ØDn) : Ø21.7
[9 empty] | □ U : Upscale burnout (Standard) | [5 empty] | * Lead wire length : 200 (mm)
□ D : Downscale burnout
** Note. Connector type(Standard) / Drilled bar(only for nipple length 100mm)
|  | *The Colors of each wires can be replaced with the ones of the user's choice. | [6 empty] | This drawing and the specifications are |  |  |  | THIRD ANGLE PROJECTION
|  | *Use PVC standard colors | [6 empty] | the intellectual property of WISE
|  |  |  | ELEMENT TYPE | □ ANSI |  | □ JIS( KS ) |  | CONTROL INC. Therefore, without a prior
[5 empty] | + | - | + | - | written consent from WISE CONTROL INC.,
|  |  |  | K | YELLOW | RED | RED | WHITE | it is strictly prohibited to reproduce the | [7 empty] | WISE Control Inc.
|  |  |  | E | PURPLE | RED | RED | WHITE | drawing or manufacture the identical
|  |  |  | J | WHITE | RED | RED | WHITE | products according to its specifications |  |  |  |  | SIGNATURE | DATE |  | DRAWING TITLE : |  | Smart temperature Transmitter
|  |  |  | T | BLUE | RED | RED | WHITE | provided here.
|  |  |  | B | GRAY | RED | RED | WHITE |  |  |  | PREPARED BY |  | S.M.JUNG | 2023-05-25 |  | MODEL : | SMT3000(TC)
|  |  |  | S, R | BLACK | RED | RED | WHITE
3 | [11 empty] | REVIEWED BY |  | H.J.KIM | 2023-05-25 |  | PROJECT : -
2
1 | [11 empty] | APPROVED BY |  | H.J.KIM | 2023-05-25 |  | DWG NO. : | SMT3000B-UN-001(TC)
NO | REASON |  | DATE | PREPARED BY | REVIEWED BY |  | APPROVED BY
REVISION | [11 empty] | REV. NO. |  | 0 |  |  | SCALE: N/S |  |  | W.T. | SHEET OF
HEAD
ELEMENT