## SMT3000C-FT-001(TC)
GENERAL SPECIFICATION
[17 empty] | 1. Power supply | WTT-3000 : 10~32V DC
iTEMP TMT82 : 11~42V DC
Rosemount 644H : 12~42.4V DC
2. Output : 4 ~ 20mA with HART Protocol
3. Housing Material : ADC12
4. Protection grade : IP66&IP67
[17 empty] | 5. Certificates | □ None |  | □ 1 : KCs Ex db llC T6 Gb
*Sleeve
Out dia.(Ød)(mm) : ■ 12 □ Other
Length "T"(mm) : ■ 50 □ Other
*Flexible tube length "A" : mm
*Insulation material for lead wires
[17 empty] | □ A : PVC | □ B : Teflon |  | □ D : Outer shield
ORDERING INFORMATION
| 1. Base model : SMT3000(Smart temperature taransmitter) | [10 empty] | 7. Mounting type |  |  |  |  | 12. Display
| 2. Type : ■ C : Remote type | [10 empty] | ■ X : Fixed thread |  |  |  |  | □ A : PV (Temperature ˚C, ˚F)
| 3. Element(Tolerance) | [10 empty] | 8. Connection size & material |  |  |  |  | □ B : Current (4~20 mA)
| □ K : K(0.75) |  | □ J : J(0.75) |  |  | □ T : T(0.75) | [5 empty] | □ EB : PT 1/2"(304SS) | □ EC : NPT 1/2"(304SS) |  |  |  | □ C : Persent (0~100%)
| □ N : N(0.75) |  | □ E : E(0.5) | [8 empty] | □ RB : PT 1/2"(316SS) | □ RC : NPT 1/2"(316SS) |  |  |  | 13. Burnout mode
| □ B : B(0.5) |  | □ R : R(0.25) |  |  | □ S : S(0.25) | [5 empty] | □ ED : PF 1/2"(304SS) | □ RD : PF 1/2"(316SS) |  |  |  | □ U : Upscale burnout (Standard)
| □ 1 : K(0.4) |  | □ 2 : J(0.4) |  |  | □ 3 : T(0.4) | [5 empty] | 9. Insert length "L" : mm |  |  |  |  | □ D : Downscale burnout
| □ 5 : N(0.4) |  | □ 4 : E(0.4) | [8 empty] | * Lead wire length : 200 (mm) |  |  |  |  | * Note.
| 4. Sheath material | [10 empty] | 10. Temperature transmitter |  |  |  |  | Adapters are applied for all sizes other than M20(St'd).
| □ 2 : Inconel 600 |  |  | □ 3 : 310SS |  |  | □ 4 : 446SS |  |  |  |  | □ A : WTT-3000 (WISE) |  |  |  |  | If explosion-proof certification is requested,
| □ 5 : 347SS |  |  | □ 6 : 321SS |  |  | □ 7 : 316L SS |  |  |  |  | □ B : iTEMP TMT82 (Endress+Hauser) |  |  |  |  | an explosion-proof adapter is applied.
| 6. Conduit connection |  |  | □ With adaptor |  |  | □ None |  |  |  |  | □ C : Rosemount 644 (EMERSON) |  |  |  |  | Additional clamping of cable shall be installed to ensure
| □ 1 : PF 1/2" |  | □ 3 : NPT 1/2" |  |  | □ 8 : M20x1.5P (St'd) |  |  | □ 9 : Other |  |  | 11. Measuring range (˚C) : |  |  |  |  | that pulling and twisting is not transmitted to the terminal.
* Adaptor Material : □ 316SS □ Brass+Ni □ 304SS(Only weatherproof)
|  |  |  | *The Colors of each wires can be replaced with the ones of the user's choice. | [7 empty] | This drawing and the specifications are |  |  | THIRD ANGLE PROJECTION
|  |  |  | *Use PVC standard colors | [7 empty] | the intellectual property of WISE
[7 empty] | ELEMENT TYPE | □ ANSI |  | □ JIS( KS ) |  | CONTROL INC. Therefore, without a prior
[8 empty] | + | - | + | - | written consent from WISE CONTROL INC.,
[7 empty] | K | YELLOW | RED | RED | WHITE | it is strictly prohibited to reproduce the | [5 empty] | WISE Control Inc.
[7 empty] | E | PURPLE | RED | RED | WHITE | drawing or manufacture the identical
[7 empty] | J | WHITE | RED | RED | WHITE | products according to its specifications |  |  |  | SIGNATURE | DATE | DRAWING TITLE : |  | Smart temperature Transmitter
[7 empty] | T | BLUE | RED | RED | WHITE | provided here.
[7 empty] | B | GRAY | RED | RED | WHITE |  |  | PREPARED BY |  | S.M.JUNG | 2023-05-25 | MODEL : | SMT3000(TC)
[7 empty] | S, R | BLACK | RED | RED | WHITE
3 | [13 empty] | REVIEWED BY |  | H.J.KIM | 2023-05-25 | PROJECT : -
2
1 | [13 empty] | APPROVED BY |  | H.J.KIM | 2023-05-25 | DWG NO. : | SMT3000C-FT-001(TC)
NO | REASON |  |  |  | DATE |  | PREPARED BY | REVIEWED BY |  | APPROVED BY
REVISION | [13 empty] | REV. NO. |  | 0 |  | SCALE: N/S |  |  | W.T. | SHEET OF
HEAD
ELEMENT