## 06. SMT4210-W-S
[10 empty] | NO. | DESCRIPTION |  |  |  | MAIN MATERIAL | [6 empty] | Q`TY |  | REMARK
[10 empty] | 1 | HEAD |  |  |  | ALUMINIUM | [6 empty] | 1
[10 empty] | 2 | CONNECTOR |  |  |  | 316LSS | [6 empty] | 1
[10 empty] | 3 | PROCESS CON'N |  |  |  | 304SS |  | 304LSS |  | 316SS |  | 316LSS | 1 |  |  |  | <개정이력>
[10 empty] | 4 | GUIDE TUBE |  |  |  | 316/316LSS | [6 empty] | 1 |  |  |  | NO. | DATE | 변경 내용
[10 empty] | 5 | FLOAT |  |  |  | 316LSS | [6 empty] | 1 |  |  |  | 1 | 24.06.20 | 1" FLOAT 추가 및 3-4"용 FLOAT 의 L2값 80mm로 수정, CONNECTOR 재질 316LSS만 적용 / GUIDE TUBE 재질 316/316LSS 만 적용
[10 empty] | 6 | STOPPER |  |  |  | 316LSS | [6 empty] | 2 |  |  |  | 2
3
[10 empty] | [NOTE] | [15 empty] | 4
(1) MOUNTING TYPE : TOP
(2) ENCLOSURE : Weather Proof (IP66)
(3) WORKING TEMP. : Max. Temp. 150°C
(4) POWER SUPPLY : DC 17~36V
(5) OUTPUT SIGNAL : DC 4~20mA (2-Wire)
ORDERING INFORMATION
[10 empty] | 1. Float Size : |  |  | Float Size (ØB*H) |  |  |  | L1 |  |  | L2 |  | ØA
[13 empty] | □ | Ø28 * 28L |  |  | Min.50 |  |  | Min.30 |  | Min. Ø32
[13 empty] | □ | Ø48 * 50L |  |  | Min.50 |  |  | Min.50 |  | Min. Ø52
[13 empty] | □ | Ø65 * 90L |  |  | Min.100 |  |  | Min.80 |  | Min. Ø72
[10 empty] | 2. Conduit connection : |  |  |  | □ | C1 : M20 x 1.5P (S.T.D)
[14 empty] | □ | C2 : 1/2” NPT(F) w/Adapter
[14 empty] | □ | C3 : 3/4” NPT(F) w/Adapter
[14 empty] | □ | C4 : 1/2” PF(F) w/Adapter
[14 empty] | □ | C5 : 3/4” PF(F) w/Adapter
[14 empty] | □ | ZZ : Etc.
3
2
1
[6 empty] | NO | TAG NO. | Process Con'n |  |  |  | L1 | Measuring Range |  |  | L2 |  | TL |  | Oper./Design |  | Oper./Design |  |  | REMARK
[20 empty] | Press(kg/cm2g) |  | Temp.(°C)
[6 empty] | This drawing and the specifications are the intellectual property of WISE CONTROL INC. therefore, without a prior written consent from WISE CONTROL INC., it is strictly prohibited to reproduce the drawing or manufacture the identical products according to its specifications provided here. |  |  | THIRD ANGLE PROJECTION
5 | [16 empty] | WISE CONTROL INC.
4 | [16 empty] | DRAWING TITLE : |  |  |  | GENERAL OUTLINE DRAWING
3 | [11 empty] | SIGNATURE |  | DATE |  |  |  |  | MAGNETIC FLOAT TYPE LEVEL TRANSMITTER
2 | [5 empty] | UNLESS OtherWISE SPECIFIED DECIMAL DIMENSIONS ±5 ANGLE DIMENSIONS ±1˚ DIMENSIONS ARE IN MILLI METER |  |  | DESIGNED BY |  |  | M.J.KIM |  | 2024-06-21 |  |  | MODEL |  |  | : SMT4000 Serise
1 | [8 empty] | CHECKED BY |  |  | S.L.LEE |  | 2024-06-21 |  |  | PROJECT |  |  | :
NO | REASON | DATE | REVIEWED BY | CHECKED BY | APPROVED BY |  |  |  | APPROVED BY |  |  | H.J.KIM |  | 2024-06-21 |  |  | DWG NO. |  |  | : SMT4210-W-S
REVISION | [8 empty] | Rev. No |  |  | 0 |  |  |  |  | SCALE : N/S |  |  |  | W.T. |  | SHEET OF
5
4
3
2
1
[6 empty] | NO | TAG NO. | Process Con'n |  |  |  | L1 | Measuring Range |  |  | L2 |  | TL |  | Oper./Design |  | Oper./Design |  |  | REMARK
[20 empty] | Press(kg/cm2g) |  | Temp.(°C)
[ TOLERANCE OF MEASURING RANGE ]
-UP TO 1500 : ± 1.5
-OVER 1500 : ± 0.1%